Test and Balance Report

Project: Dr. Perrin Blank                                                                  System 1

603 Village Blvd. Suite 304

Village Commeree Center

Unit Data

Make3: Rheem                                   Make/ Frame GE/Direct Drive

Model#: 5 Ton                                   H.P./ Amps: ¾ 6.7

Serial#: N/A                                       Volts/ Phase/Hertz: 208/1/60

No. Filter/Size: N/A                           Make Sheave: N/A

Fan Sheave Diam/Bore: N/A

Heater: 7.2

Humidity: 58%

Test Data Evaporator		Design		Actual

Total CFM			2160		2062

Total S.P.			.5		.47

Out Air CFM			160		148

Ret Air CFM			N/A		1923

Test Date: 9/29/06

Air Outlet Test Report

Project: Dr. Perin Blank				System: Split System 1

Outlet Man: Titus					Test Apparatus: Flow Hood

Area		#	Size		Design		Preliminary		Final

Served					CFM		CFM			CFM

Dr. Office	1	24x24		140		157			157

Dr. Office        1	24x24		250		222			222

Dr. Office	1	24x24		175		91			91

Dr. Office	1	24x24		Return		470			470

AHU Rm	1	24x24		Return		1276			1276

Room 1S	1	24x24		220		173			173

Room 2S	1	24x24		220		150			205

Room 3S	1	24x24		220		223			223

Room 4S	1	24x24		220		259			259

Room 1N	1	24x24		135		103			103

Room 1N	1	24x24		Return		110			110

Room 2N	1	24x24		100		100			100

Room 3N	1	24x24		75		75			75

Room 3N	1	24x24		Return		77			77

Room 4N	1	24x24		50		50			50

Room 5N	1	24x24		75		53			53

Room 6N	1	24x24		50		50			50

Hallway	1	24x24		110		108			108

Hallway	1	24x24		120		144			93

Total:                                                 2,160               2,615                         2,619

Supply				           2,160	          1,958		        2,062

Return					N/A	          1,923	                    1,923

Air Outlet Test Report

Project: Dr. Perin Blank				System: Split System 2

Outlet Man: Titus					Test Apparatus: Flow Hood

Area		#	Size		Design		Preliminary		Final

Served					CFM		CFM			CFM

Room 7N	1	24x24		130		168			140

Room 7N	1	24x24		Return		141			141

Reception	1	24x24		150		272			189

Reception	1	24x24		150		215			187

Reception	1	24x24		125		96			112

Reception	1	24x24		100		104			119

Reception	1	24x24		170		109			109

Reception	1	24x24		Return		444			444

Reception	1	24x24		Return		382			382

Hallway	1	24x24		150		142			142

Room 5S	1	24x24		140		235			243

Room5S	1	24x24		150		235			243

Room 6S	1	24x24		275		170			235

Room 6S	1	24x24		Return		590			590

Total:                                                1,540	           2854	                     2,685

Supply				          1540	           1746		         1719

Return					N/A	           1557		         1557