|  | # Unit Data |  |  | # Motor Data |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Make | Trane |  | Make/Frame | General Electric/NA |  |
|  | Model Number | 4TCC3030A1000AA |  | H.P./RPM | ½ /1000 |  |
|  | Serial Number | 9322PB99H |  | Volts/Phase/Hertz | 208/1/60 |  |
|  | Make Sheave | Direct Drive |  | Full Load Amps/S.F. | 2.0/NA |  |
|  | Sheave Diam/Bore | NAP |  | Make Sheave | Direct Drive |  |
|  | No. Belts/Size | NAP |  | Sheave Diam/Bore | NAP |  |
|  |  |  |  | Sheave CL Distance | NAP |  |

Package Rooftop Unit

Test Report

Project:       Southern Park of Commerce                                                                  System:       RTU-1

Location:     Building “B”, Bay 11, West Palm Beach, Florida

|  | ## Evaporator Data | ## Design | ### Actual |  | ## Condensor Data | ### Compr #1 | ### Compr #2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Total CFM | 1400 | 1390 |  | Refrigerant/Lbs./Ozs. | 410/6/5 | NAP |  |
|  | Total E.S.P. | NA | - |  | Compr. Manufacturer | Alliance | NAP |  |
|  | Discharge S.P. | NA | - |  | Compr. Model Number | SPA026B1RPA | NAP |  |
|  | Suction S.P. | NA | - |  | Compr. Serial Number | 09D3616AN | NAP |  |
|  | Outside Air CFM | 75 | 81 |  |  |  |  |  |
|  | Outside Air DB/WB | NA | 81.2/69.6 |  |  |  |  |  |
|  | Return Air CFM |  | 904 |  |  |  |  |  |
|  | Return Air DB/WB | NA | 71.4/60.0 |  | Condensor Fan HP | 1/5 | - |  |
|  | Entering Air DB/WB | NA | 71.8/60.4 |  | No. of Fans/Fan RPM | 1/830 | - |  |
|  | Leaving Air DB/WB | NA | 55.7/55.1 |  | Cond Fan Volt/Phase/Hz | 208/1/60 | - |  |
|  | Fan RPM | NA | 1000 |  | Condensor Fan Amps | 1.1 | - |  |
|  | Motor Voltage T1T2T3 | 208 | 212 |  | Compr. Volts T1 T2 T3 | 211 | NAP |  |
|  | Motor Amperage T1 T2 T3 | 2.0 | 1.8 |  | Compr. Amps T1 T2 T3 | 14.7 | NAP |  |

Remarks:

Test Date: 12-03-09                                             Readings By: Martinez                                              Page 1 of 4