Air Outlet

Test Report

Project:       Southern Park of Commerce                                                                  System:       RTU-1

Location:     Building “B”, Bay 11, West Palm Beach, Florida                                      Test Apparatus:  Flowhood

| ### Area Served/ Room Number | No. | ### Type | ### Size | ### Design CFM | ### Prelim CFM | ### Prelim CFM |  | ### Final CFM | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SUPPLY AIR |  |  |  |  |  |  |  |  |  |
| Office | 1 | CD | 24X24 | 475 | 442 |  |  | 455 |  |
| Office | 2 | CD | 24X24 | 475 | 443 |  |  | 452 |  |
| Restroom | 3 | CD | 6X4 | 50 | 88 |  |  | 51 |  |
| SUPPLY TOTAL |  |  |  | 1000 |  |  |  | 958 |  |

Remarks:

Test Date: 12-03-09                                             Readings By: Martinez                                              Page 2 of 4