BUilding Technology Svcs, inc. license# cac058685

13833 WELLINGTON TRACE, E4-157 WELLINGTON, FL. 33414 561-712-1126 fax 561-712-1407

August 7, 2013

One World Realty, Inc.

1250 North Ocean Drive

Singer Island, FL. 33404

Attn: Nancy Lubeck

PROJECT: 1102 CABANA ROAD, COMPRESSOR REPLACEMENT

We hereby submit specifications and estimate to:

Provide and install; (1) Trane COM10025 compressor for condensing unit model# 2TTB3036A1000AA/serial # 6415KJ13F, (1) liquid line filter/drier, (1) suction line filter/drier, system flush, acid neutralizer and a full charge of virgin R-422D refrigerant.

Note: Existing compressor has suffered an electrical burnout which means all existing refrigerant is not usable, system is full of acid created by the burning refrigerant, and steps must be taken to prevent premature failure of the new compressor. Necessary steps are reflected in this quote.

Price…………………$1,590.64

Price to include: Labor, and miscellaneous materials.

Price does not include: After-hours labor or anything not specified above.

Thank you,

Robert Campbell,

B.T.S., Inc.