BUilding Technology Svcs, inc.

facsimile transmittal sheet

| to: |  | from: |
| --- | --- | --- |
| Luv |  | Rob C. |
| company: |  | date: |
| Turbo Air |  | 7/12/13 |
| fax number: |  | total no. of pages including cover: |
| 310-900-1033 |  | 2 |
| Phone number: |  | sender’s reference number: |
| 310-900-1030 |  |  |
| Re: |  | Your reference number: |
| Warranty compressor |  |  |

 Urgent	 For Review	 Please Comment	X Please Reply	 Please Recycle

notes/Comments:

Re: Freezer model #M3F47-2  serial #M3F4L47020

I found the above noted freezer at 50 deg. F with the compressor running and an amp draw of 10.2A with pressures of 100 low x 180 high. After measuring temps at several locations and noting a foul (not phosgene) smell in the refrigerant, I removed all of the refrigerant, evacuated the system and added virgin R404a. My operating pressures were then 115 low x 205 high. After measuring temps at several locations and speaking with your tech support guy, I condemned the compressor as having a problem with the valve(s) or the internal relief. Hot gas is obviously bleeding into the low pressure side in the compressor.

I have attached the page of the invoice from Delray Foodservice Equipment which lists the freezer.

Please ship the compressor to our physical address:

Building Technology Services, Inc.

1520 Buckingham Avenue

Wellington, FL. 33414

13833 Wellington trace e4-157 wellington florida 33414 561-712-1126 fax 712-1407

Any questions, please call my cell- 561-718-5380.

Please fax or email to 561-712-1407 or   rob@bts-ac.com

Thank you.