|  | # Unit Data |  |  | # Motor Data |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Make | FHP |  | Make/Frame | GE/Direct Drive |  |
|  | Model Number | EM024-2 |  | H.P./RPM | ¼/1075 |  |
|  | Serial Number | CF880557 |  | Volts/Phase/Hertz | 277/1/60 |  |
|  | Make Sheave | NA |  | Full Load Amps/S.F. | 1.6/1.8 |  |
|  | Sheave Diam/Bore | NA |  | Make Sheave | NA |  |
|  | No. Belts/Size | NA |  | Sheave Diam/Bore | NA |  |
|  |  |  |  | Sheave CL Distance | NA |  |

Water Source Heat Pump

Test Report

Project:       Alan Gould                                                                                             System:       HP-1

Location:    1601 Forum Place, #600 West Palm Beach, Florida

|  | ## Evaporator Data | ## Design | ### Actual |  | ## Condensor Data | ### Compr #1 | ### Compr #2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Total CFM | 650 | 695 |  | Refrigerant/Lbs./Ozs. | 22/4/1 |  |  |
|  | Total E.S.P. | NA | - |  | Compr. Manufacturer | Copeland |  |  |
|  | Discharge S.P. | NA | - |  | Compr. Model Number | CR24KQTF5230 |  |  |
|  | Suction S.P. | NA | - |  | Compr. Serial Number | 88DC6570L |  |  |
|  | Outside Air CFM | 62 | 65 |  | Condensor EWT | 88.5 |  |  |
|  | Outside Air DB/WB | NA | 84.8/73.1 |  | Condensor LWT | 100.1 |  |  |
|  | Return Air CFM | 588 | 630 |  | Condensor GPM | 5.5 |  |  |
|  | Return Air DB/WB | NA | 74.3/62.6 |  | Condensor Fan HP | NA |  |  |
|  | Entering Air DB/WB | NA | 74.9/64.0 |  | No. of Fans/Fan RPM | NA |  |  |
|  | Leaving Air DB/WB | NA | 58.5/58.9 |  | Cond FanVolt/Phase/Hz | NA |  |  |
|  | Fan RPM | 1075 | 1075 |  | Condensor Fan Amps | NA |  |  |
|  | Motor VoltageT1T2T3 | 265 | 278 |  | Compr. Volts T1 T2 T3 | 278 NA NA |  |  |
|  | Motor Amperage T1 T2 T3 | 1.6 | 1.3 |  | Compr. Amps T1 T2 T3 | 7.2 NA NA |  |  |

Remarks:

Test Date: 11-30-12                                             Readings By: Martinez                                              Page 1 of 4