|  | # Unit Data |  |  | # Motor Data |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Make | FHP |  | Make/Frame | GE/Direct Drive |  |
|  | Model Number | EM036-4 |  | H.P./RPM | ½/1100 |  |
|  | Serial Number | HE010318 |  | Volts/Phase/Hertz | 460/1/60 |  |
|  | Make Sheave | NA |  | Full Load Amps/S.F. | 2.0/2.25 |  |
|  | Sheave Diam/Bore | NA |  | Make Sheave | NA |  |
|  | No. Belts/Size | NA |  | Sheave Diam/Bore | NA |  |
|  |  |  |  | Sheave CL Distance | NA |  |

Water Source Heat Pump

Test Report

Project:       Alan Gould                                                                                             System:       HP-2

Location:    1601 Forum Place, #600 West Palm Beach, Florida

|  | ## Evaporator Data | ## Design | ### Actual |  | ## Condensor Data | ### Compr #1 | ### Compr #2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Total CFM | 1175 | 1067 |  | Refrigerant/Lbs./Ozs. | 22/6/4 |  |  |
|  | Total E.S.P. | NA | - |  | Compr. Manufacturer | Copeland |  |  |
|  | Discharge S.P. | NA | - |  | Compr. Model Number | CR36K3PF4812 |  |  |
|  | Suction S.P. | NA | - |  | Compr. Serial Number | 01FK2648T |  |  |
|  | Outside Air CFM | 43 | 40 |  | Condensor EWT | 88.3 |  |  |
|  | Outside Air DB/WB | NA | 84.8/73.1 |  | Condensor LWT | 104.3 |  |  |
|  | Return Air CFM | 1132 | 1027 |  | Condensor GPM | NA |  |  |
|  | Return Air DB/WB | NA | 74.3/62.6 |  | Condensor Fan HP | NA |  |  |
|  | Entering Air DB/WB | NA | 74.5/63.8 |  | No. of Fans/Fan RPM | NA |  |  |
|  | Leaving Air DB/WB | NA | 57.6/58.1 |  | Cond FanVolt/Phase/Hz | NA |  |  |
|  | Fan RPM | 1100 | 1100 |  | Condensor Fan Amps | NA |  |  |
|  | Motor VoltageT1T2T3 | 460 | 485 |  | Compr. Volts T1 T2 T3 | 488 485 485 |  |  |
|  | Motor Amperage T1 T2 T3 | 2.0 NA NA | 1.6 NA NA |  | Compr. Amps T1 T2 T3 | 4.5 4.6 4.6 |  |  |

Remarks:

Test Date: 11-30-12                                             Readings By: Martinez                                              Page 2 of 4