Air Outlet

Test Report

Project:       Alan Gould                                                                                              System:       HP-1

Location:    1601 Forum Place, #600 West Palm Beach, Florida                              Test Apparatus:  Flowhood

| ### Area Served/ Room Number | No. | ### Type | ### Size | ### Design CFM | ### Prelim CFM | ### Prelim CFM |  | ### Final CFM | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SUPPLY AIR |  |  |  |  |  |  |  |  |  |
| Office 101 | 1 | CD | 24X24 | 125 | 140 |  |  | 125 |  |
| CL 104 | 2 | CD | 24X24 | 25 | 92 |  |  | 28 |  |
| Office 102 | 3 | CD | 24X24 | 125 | 217 |  |  | 138 |  |
| CORR | 4 | CD | 24X24 | 75 | 152 |  |  | 83 |  |
| Reception 100 | 5 | CD | 24X24 | 150 | 176 |  |  | 162 |  |
| Reception 100 | 6 | CD | 24X24 | 150 | 90 |  |  | 159 |  |
| Supply Total |  |  |  | 650 |  |  |  | 695 |  |

Remarks:

Test Date: 11-30-12                                             Readings By: Martinez                                              Page 3 of 4