Air Outlet

Test Report

Project:       Alan Gould                                                                                              System:       HP-2

Location:    1601 Forum Place, #600 West Palm Beach, Florida                              Test Apparatus:  Flowhood

| ### Area Served/ Room Number | No. | ### Type | ### Size | ### Design CFM | ### Prelim CFM | ### Prelim CFM |  | ### Final CFM | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SUPPLY AIR |  |  |  |  |  |  |  |  |  |
| Break 105 | 1 | CD | 24X24 | 275 | 227 |  |  | 251 |  |
| Office 106 | 2 | CD | 24X24 | 200 | 2 |  |  | 180 |  |
| Office 106 | 3 | CD | 24X24 | 200 | 217 |  |  | 182 |  |
| Office 107 | 4 | CD | 24X24 | 250 | 152 |  |  | 229 |  |
| Office 107 | 5 | CD | 24X24 | 250 | 176 |  |  | 225 |  |
| Supply Total |  |  |  | 1175 |  |  |  | 1067 |  |

Remarks:

Test Date: 11-30-12                                             Readings By: Martinez                                              Page 4 of 4