BUilding Technology Svcs, inc. license# cac058685

13833 WELLINGTON TRACE, E4-157 WELLINGTON, FL. 33414 561-712-1126 fax 561-712-1407

April 9, 2010

Fisher Contracting Corp.

4440 PGA Blvd. Suite 403

Palm Beach Gardens, FL. 33410

PROJECT: SPOC-BAY 6 MODIFICATIONS

We hereby submit specifications and estimate to:

Remove; (3) Titus extruded aluminum sidewall grilles with integral OBD’s on the two supply grilles. Re-configure/add transfer air ductwork to accommodate new transfer grille in wall. In-house test and balance limited to balancing of new supply drops and re-balancing of existing supply drops.

Price…………………$550.00

Price to include: Labor, and miscellaneous materials.

Price does not include: Anything not specifically stated above.

Note: The trunk lines to which the supply grilles are being added are 16x12 as per the plan revision and not 20x12 as shown on the original plans, which we are now trying to implement. This should however not be a significant issue (from a performance standpoint) as only 17x12 is truly required to meet the design cfm shown on the original plan and we still have an extra 200 cfm as the total cfm from the RTU is 2,800 and only 2,600 total are shown as being delivered at the supply grilles. These factors should make for an insignificant variation from design airflow at the supply grilles, but it is still a deviation from the original plan’s design and a deviation (albeit small) from standard industry practice.

Thank you,

Robert Campbell,

B.T.S., Inc.