|  | # Unit Data |  |  | # Motor Data |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Make | Carrier |  | Make/Frame | GE/56Y |  |
|  | Model Number | 50HJ008V531 |  | H.P./RPM | NA/1725 |  |
|  | Serial Number | 1609G10721 |  | Volts/Phase/Hertz | 208/3/60 |  |
|  | Make Sheave | Fennis |  | Full Load Amps/S.F. | 7.5/8.4 |  |
|  | Sheave Diam/Bore | 7”/1” |  | Make Sheave | Power Drive |  |
|  | No. Belts/Size | 1/A-49 |  | Sheave Diam/Bore | 5”/7/8” |  |
|  |  |  |  | Sheave CL Distance | 3/8” |  |

Package Rooftop Unit

Test Report

Project:       Southern Park of Commerce                                                                  System:       RTU-2

Location:     Building “B”, Bay 6, West Palm Beach, Florida

|  | ## Evaporator Data | ## Design | ### Actual |  | ## Condensor Data | ### Compr #1 | ### Compr #2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Total CFM | 3000 | 3075 |  | Refrigerant/Lbs./Ozs. | 22/7/9.6 | 22/8/1.6 |  |
|  | Total E.S.P. | NA | - |  | Compr. Manufacturer | Copeland | Copeland |  |
|  | Discharge S.P. | NA | - |  | Compr. Model Number | ZR42K3TF5230 | ZR42K3TF5230 |  |
|  | Suction S.P. | NA | - |  | Compr. Serial Number | 09DC6416L | 09DC6370L |  |
|  | Outside Air CFM | 200 | 201 |  |  |  |  |  |
|  | Outside Air DB/WB | NA | 84.8/73.1 |  |  |  |  |  |
|  | Return Air CFM | 2800 | 2823 |  |  |  |  |  |
|  | Return Air DB/WB | NA | 73.6/61.8 |  | Condensor Fan HP | ¼ | ¼ |  |
|  | Entering Air DB/WB | NA | 74.0/62.2 |  | No. of Fans/Fan RPM | 2/1100 | 2/1100 |  |
|  | Leaving Air DB/WB | NA | 57.4/57.7 |  | Cond FanVolt/Phase/Hz | 208/1/60 | 208/1/60 |  |
|  | Fan RPM | NA | 1725 |  | Condensor Fan Amps | 1.4 | 1.4 |  |
|  | Motor VoltageT1T2T3 | 208 | 209 |  | Compr. Volts T1 T2 T3 | 209 209 209 | 209 209 209 |  |
|  | Motor Amperage T1 T2 T3 | 7.5 7.5 7.5 | 7.2 7.2 7.1 |  | Compr. Amps T1 T2 T3 | 12.0 12.1 12.0 | 12.1 11.9 12.0 |  |

Remarks:

Test Date: 12-01-09                                             Readings By: Martinez                                              Page 2 of 5