Air Outlet

Test Report

Project:       Southern Park of Commerce                                                                  System:       RTU-1

Location:     Building “B”, Bay 6, West Palm Beach, Florida                                      Test Apparatus:  Flowhood

| ### Area Served/ Room Number | No. | ### Type | ### Size | ### Design CFM | ### Prelim CFM | ### Prelim CFM |  | ### Final CFM | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SUPPLY AIR |  |  |  |  |  |  |  |  |  |
| Sales Counter | 1 | OBD | 14X10 | 600 | 720 |  |  | 640 |  |
| Sales Counter | 2 | OBD | 14X10 | 600 | 735 |  |  | 647 |  |
| Sales Counter | 3 | OBD | 14X10 | 600 | 728 |  |  | 649 |  |
| Sales Counter | 4 | OBD | 14X10 | 600 | 731 |  |  | 641 |  |
| Lower Office (Triangle) | 5 | CD | 24X24 | 120 | 111 |  |  | 128 |  |
| Lower Office (Square) | 6 | CD | 24X24 | 250 | 258 |  |  | 263 |  |
| Restroom-M | 7 | CD | 24X24 | 25 | 64 |  |  | 28 |  |
| Restroom-F | 8 | CD | 24X24 | 25 | 58 |  |  | 29 |  |
| Supply Total |  |  |  | 2820 |  |  |  | 3025 |  |

Remarks:

Test Date: 12-01-09                                             Readings By: Martinez                                              Page 3 of 5