Air Outlet

Test Report

Project:       Southern Park of Commerce                                                                  System:       RTU-   1

Location:     Building “B”, Bay 12, West Palm Beach, Florida                                      Test Apparatus:  Flowhood

| ### Area Served/ Room Number | No. | ### Type | ### Size | ### Design CFM | ### Prelim CFM | ### Prelim CFM |  | ### Final CFM | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SUPPLY AIR |  |  |  |  |  |  |  |  |  |
| Upper Office | 1 | CD | 24X24 | 280 | 285 |  |  | 285 |  |
| Lower Office (Inner) | 2 | CD | 24X24 | 380 | 343 |  |  | 365 |  |
| Lower Office (Outer) | 3 | CD | 24X24 | 335 | 348 |  |  | 337 |  |
| Lower Office (Outer) | 4 | CD | 24X24 | 335 | 359 |  |  | 334 |  |
| Restroom | 5 | CD | 6X6 | 70 | 88 |  |  | 69 |  |
| SUPPLY TOTAL |  |  |  | 1400 |  |  |  | 1390 |  |

Remarks:

Test Date: 12-01-09                                             Readings By: Martinez                                              Page 2 of 4