BUilding Technology Svcs, inc. license# cac058685

2257 Vista parkway, suite 20 west palm beach fl 33411 561-712-1126 fax 561-712-1407

R.F.I.

January 19, 2007

Catalfumo Construction

4300 Catalfumo Way

Palm Beach Gardens, FL. 33410

PROJECT: CANNONSPORT MARINA CONDOS

We hereby submit the following request for information for the above named project:

- Please provide a roof mounting detail for the BESB-250 Box Ventilator which is a component of the Exhausto dryer venting system. The BESB-250 is shown as “MDVS-1” on the mechanical roof plan pages (HX-4). Also include details for attaching, sealing, and supporting the ductwork, which penetrates up through the roof, travels a distance horizontally across the roof, and then is connected to the BESB-250. I have attached a copy of the BESB Installation and Operating Manual for your reference.

- Please provide a detail for supporting/anchoring of refrigerant line-sets where they will run horizontally across the roof, from the roof penetrations to the condensing units.

- Please refer to the plan pages H2-1A and H2-1B. “E/F-5” is shown in (1) location on pg. H2-1A and (2) locations on pg. H2-1B. E/F-5 as it is shown on pg. H2-1A is bringing air into the building, rather than exhausting it, and it is not shown with a louver as they are shown with on pg. H2-1B. Clarify the orientation of E/F-5 on pg. H2-1A and whether or not a louver is desired.

- In reference to E/F-5, the specified wall sleeve, back draft damper, and louver: The wall thickness on this project is 8 inches. The specified louver (Ruskin ELF6375DX) is 6 inches deep, the back draft damper is 6-1/4 inches deep when the damper is open and the fan itself will take up some space in the wall cavity. Clearly some type of extrusion will need to be designed, fabricated and installed to accommodate the above items in an 8 inch wall. Please provide design and installation detail for same.

- Please refer to plan page H4-4, and look at notes #2 (range exhaust) and #3 (vent air). We cannot achieve a 10 foot minimum distance between the exhaust and vent air as they are physically closer than that to each other. Provide a design or detail which will allow us to meet code while these risers are in such close proximity to each other.

Thank you, Robert Campbell