BUilding Technology Svcs, inc. license# cac058685

13833 WELLINGTON TRACE, E4-157 WELLINGTON, FL. 33414 561-712-1126 fax 561-712-1407

December 6, 2013

Coola Fishbar

11340 Legacy Ave. #E-100

Palm Beach Gardens, FL. 33410

BAR A/C: COMPRESSOR #2

We hereby submit specifications and estimate to:

Provide and install; (1) OEM Copeland Scroll 3-phase compressor, 9.5 lbs. of R-22, system flush, acid neutralizer, liquid line filter/drier.

Price…………………$1,799.00

Price to include: Recovery and disposal of acidic (burnt) refrigerant in circuit, disposal of old compressor, acetylene, oxygen, 15% silver brazing sticks, vacuum pump oil, miscellaneous materials, labor, 90-day warranty, and applicable discounts under service agreement.

Price does not include: After-hours labor or anything not specified above.

Note: System flush, acid neutralizer, recovery/disposal of burnt refrigerant, and 9.5 lbs. of new refrigerant are necessary due to fact that the compressor was electrically shorting over a period of days which burnt the refrigerant and creating phosgene (acid) gas.

Thank you,

Robert Campbell,

B.T.S., Inc.